AFD Series

Overview

The AFD Series is a polypropylene metallized film

with cylindrical aluminium can type filled with resin,

screw terminals and plastic deck.

Application:

AFD capacitor for general use in power electronics,

Some typical examples of AC filter applications are as

follows: solar power, Inverter, UPS, wind power, etc.

Characteristics

Standard capacitance tolerance                  J: ± 5%

Dielectric dissipation factor (tan δo)               2 x 10-4

Minimum temperature Θmin.                    –40 °C

Maximum temperature Θmax.                   + 70 °C

Storage temperature Θstg                      –40 ... +85 °C

Maximum hotspot temperature Θhs              +70 ºC

Climatic category                             40/70/56

Permissible Relative Humidity                   Annual average ≤ 70%; 85% on 30 days/year randomly distributed throughout the year. Dewing not admissible.

Maximum altitude                             3000 m above sea level

(derating curves available upon request)

Expected lifetime                             100 000 h at Urms @ Θhs 60°C

Capacitance drop at end of life                   - 5% (typical)

Fit rate                                    100 (100 000 h at Θhs 60°C)

Reference standards

IEC 61071 , IEC 60068 , UL 810

RoHS compliance

Test data

Test voltage between terminals                   UTT  1.5 Urms , 10s

Test voltage between terminals and case            UTC  3500 VAC, 10s

Dissipation factor tan δ (100 Hz)                  ≤ 2.0 x 10-3

Self inductance (Ls)                            ≤ 60 nH

Insulation Resistance                          Ri x C ≥ 10,000s at 100 VDC/1min at +25°C

Life test According to                          IEC 61071

Design data

Impregnation Resin filling:                 Non PCB, dry type

Protection                             Aluminium case with or without, threaded bolt M12

Plastic deck flame retardant execution UL 94 V–0

Thermosetting resin sealing UL 94 V–0 compliant

Cooling                               Naturally air-cooled (or forced air cooling)

Degree of protection                     Indoor mounting

Installation                            Any position

AFD Series

Max. torque (case)                       M12 stud 8 Nm

Max. torque terminal                     internal thread M5: 2.5 Nm

internal thread M6: 4.5 Nm

Over-Voltage (IEC 61071)

1.1 x UNDC for maximum 8 Hour per day

1.15 x UNDC for maximum 30 minimum per day

1.2 x UNDC for maximum 5 minimum per day

1.3 x UNDC for maximum 1 minimum per day

1.5 x UNDC for 30 ms no more than 1000 times

Structure of ordering code

AFD – 400 – 200 – 086  0

1    2    3   4   5

1  Series code

2  rms voltage: 400 V

3  Rated capacitance: 200 μF

4  Designs Type

5  Internal use

Designs 086

Capacitors with a can diameter of 86mm

Can material          aluminium, filled with resin

Base mounting stud     M12

Lid                 plastic (UL94-V0)

Terminals            internal thread M6 x10mm

Imax (Terminals)       75A

K                  38mm

L                  20mm

AFD Series

Designs 116

Capacitors with a can diameter of 116mm

Can material          aluminium, filled with resin

Base mounting stud     M12

Lid                 plastic (UL94-V0)

Terminals            internal thread M6 x10mm

Imax (Terminals)      100A

K                  53mm

L                  35mm

Urms 750V    UNDC 1500V    Us 2200V     UTT 1125VAC/10s     UTC 3500VAC/10s

| Ordering code | Cn (μF) | Imax1 (A) | Ipk (KA) | ESR2 (mΩ) | Rth (K/W) | D (mm) | L (mm) | Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AFD-750-27-0860 | 27 | 40 | 1.5 | 2.2 | 4.2 | 86 | 95 | 0.7 |
| AFD-750-40-0860 | 40 | 40 | 1.6 | 2.6 | 3.5 | 86 | 120 | 0.9 |
| AFD-750-56-0860 | 56 | 65 | 3.2 | 1.2 | 2.4 | 86 | 174 | 1.3 |
| AFD-750-80-0860 | 80 | 65 | 3.3 | 1.4 | 1.8 | 86 | 225 | 1.5 |
| AFD-750-100-1160 | 100 | 80 | 5.7 | 0.8 | 1.7 | 116 | 178 | 2.5 |
| AFD-750-140-1160 | 140 | 80 | 5.7 | 0.9 | 1.3 | 116 | 228 | 3.0 |

1.Imax @ ΘA 40°C, that lead to a ΔT of ~ 60°C in the hotspot, Θhs =ΘA + ΔT

2.Test at 1kHz